## Incident Energy Model-Data
Data set used for Minitab Analysis of Data - IEEE 1584 Working Group
Incident Energy equation analysis
Test Set | RepGrp | VoltClass | Open/Box | Voltage OC (kv) | Log(Ibf) [Ibf in kA] | X/R | ElectrGap (mm) | Incident energy,max (cal/cm²) | Log(IncEnergy) | fit_logIarc | System Grounding | Box_code | Ground_code | Residual | Coeff | Fit | lowerPredLim | UpperPredLim | delta | safety factor
Paper Vol 36-1 | 1 | L | Open | 0.614 | 1.6119 | * | 32 | 6.2815 | 0.79802 | 1.3861 | N | 0 | 0 | 0.056151 | -0.79196 | 0.74187 | 0.46761 | 1.0161 | 0.27426 | 1.8804
Paper Vol 36-1 | 2 | L | Box | 0.612 | 1.6232 | * | 32 | 16.3348 | 1.2113 | 1.4508 | N | 1 | 0 | 0.16211 | 0.23736 | 1.0492 | 0.77685 | 1.3216 | 0.27236 | 1.8722
Kinectrics 2001 | 3 | L | Box | 0.6 | -0.17328 | 40 | 32 | 0.1192 | -0.92377 | -0.17776 | N | 1 | 0 | -0.21205 | -0.11315 | -0.71172 | -0.99518 | -0.42826 | 0.28346 | 1.9207
Kinectrics 2001 | 4 | L | Box | 0.6 | 0.54133 | 25 | 32 | 1.9307 | 0.28154 | 0.4653 | N | 1 | 0 | 0.29795 | 1.0812 | -0.01641 | -0.29063 | 0.25781 | 0.27422 | 1.8803
Kinectrics 2001 | 5 | L | Box | 0.59 | 0.52504 | 25 | 10 | 1.7307 | 0.2382 | 0.47032 | Y | 1 | 1 | 0.38645 | 0.0011 | -0.14825 | -0.42441 | 0.12791 | 0.27616 | 1.8887
Kinectrics 2001 | 6 | L | Box | 0.59 | 0.52504 | 25 | 40 | 1.561 | 0.19095 | 0.43818 | N | 1 | 0 | 0.22792 |  | -0.03697 | -0.31105 | 0.2371 | 0.27407 | 1.8796
Kinectrics 2001 | 7 | L | Box | 0.59 | 0.52504 | 25 | 40 | 1.446 | 0.15864 | 0.43818 | Y | 1 | 1 | 0.30876 |  | -0.15012 | -0.42617 | 0.12593 | 0.27605 | 1.8882
Kinectrics 2001 | 8 | L | Box | 0.59 | 0.52504 | 25 | 10 | 1.147 | 0.05873 | 0.47032 | N | 1 | 0 | 0.09383 |  | -0.0351 | -0.31109 | 0.24088 | 0.27598 | 1.8879
Kinectrics 2001 | 9 | L | Box | 0.59 | 1.4771 | 6.5 | 10 | 6.6333 | 0.82029 | 1.3855 | N | 1 | 0 | -0.13413 |  | 0.95442 | 0.68126 | 1.2276 | 0.27316 | 1.8757
Kinectrics 2001 | 10 | L | Box | 0.59 | 1.4771 | 6.5 | 40 | 6.736 | 0.82808 | 1.2664 | N | 1 | 0 | -0.030498 |  | 0.85858 | 0.58722 | 1.1299 | 0.27136 | 1.8679
Kinectrics 2001 | 11A | L | Box | 0.59 | 1.4771 | 6.5 | 10 | 5.641 | 0.74991 | 1.3855 | N | 1 | 0 | -0.20451 |  | 0.95442 | 0.68126 | 1.2276 | 0.27316 | 1.8757
Kinectrics 2001 | 11B | L | Box | 0.59 | 1.4771 | 6.5 | 10 | 5.919 | 0.77218 | 1.3855 | Y | 1 | 1 | -0.069094 |  | 0.84127 | 0.56756 | 1.115 | 0.27372 | 1.8781
Kinectrics 2001 | 12 | L | Box | 0.59 | 1.4771 | 6.5 | 10 | 9.7977 | 0.99002 | 1.3855 | N | 1 | 0 | 0.0356 |  | 0.95442 | 0.68126 | 1.2276 | 0.27316 | 1.8757
Kinectrics 2001 | 13 | L | Box | 0.59 | 1.4771 | 6.5 | 40 | 10.388 | 1.0165 | 1.2664 | Y | 1 | 1 | 0.27108 |  | 0.74543 | 0.47173 | 1.0191 | 0.2737 | 1.878
Kinectrics 2001 | 14 | L | Box | 0.25 | 1.301 | 7 | 10 | 3.3816 | 0.52881 | 0.93623 | Y | 1 | 1 | 0.17331 |  | 0.35551 | 0.08223 | 0.62879 | 0.27328 | 1.8762
Kinectrics 2001 | 15 | L | Box | 0.405 | 1.0531 | 10 | 25 | 2.568 | 0.40589 | 0.81099 | Y | 1 | 1 | 0.16935 |  | 0.23654 | -0.03691 | 0.50999 | 0.27345 | 1.8769
Kinectrics 2001 | 16 | L | Box | 0.59 | 0.43136 | 30 | 10 | 0.9597 | -0.01947 | 0.38027 | Y | 1 | 1 | 0.22614 |  | -0.24561 | -0.52271 | 0.03149 | 0.2771 | 1.8928
Kinectrics 2001 | 17 | L | Box | 0.59 | 0.43136 | 30 | 40 | 1.0233 | 0.00811 | 0.35668 | N | 1 | 0 | 0.1332 |  | -0.12509 | -0.40001 | 0.14983 | 0.27492 | 1.8833
Kinectrics 2001 | 18 | L | Box | 0.59 | 0.43136 | 30 | 40 | 0.8982 | -0.0498 | 0.35668 | Y | 1 | 1 | 0.18844 |  | -0.23824 | -0.51509 | 0.03862 | 0.27686 | 1.8917
Kinectrics 2001 | 19 | L | Box | 0.59 | 0.43136 | 30 | 10 | 0.688 | -0.16474 | 0.38027 | N | 1 | 0 | -0.032271 |  | -0.13247 | -0.40943 | 0.14449 | 0.27696 | 1.8922
Kinectrics 2001 | 20 | L | Box | 0.59 | 1.3304 | 7 | 10 | 4.135 | 0.61617 | 1.2445 | Y | 1 | 1 | -0.072624 |  | 0.6888 | 0.41556 | 0.96204 | 0.27324 | 1.876
Kinectrics 2001 | 21 | L | Box | 0.59 | 1.3304 | 7 | 40 | 5.5183 | 0.74153 | 1.1388 | N | 1 | 0 | 0.020947 |  | 0.72058 | 0.44951 | 0.99165 | 0.27107 | 1.8667
Kinectrics 2001 | 22 | L | Box | 0.59 | 1.3304 | 7 | 40 | 8.2463 | 0.91606 | 1.1388 | Y | 1 | 1 | 0.30862 |  | 0.60744 | 0.33407 | 0.8808 | 0.27336 | 1.8766
Kinectrics 2001 | 23 | L | Box | 0.59 | 1.3304 | 7 | 10 | 7.163 | 0.85404 | 1.2445 | N | 1 | 0 | 0.052101 |  | 0.80194 | 0.5292 | 1.0747 | 0.27274 | 1.8739
Square D 2002 | 24 | L | Box | 0.6 | 1.3471 | 5.465 | 38.1 | 4.3615 | 0.6396 | 1.1686 | Y | 1 | 1 | 0.002034 |  | 0.63757 | 0.36423 | 0.91091 | 0.27334 | 1.8765
Square D 2002 | 25 | L | Box | 0.4 | 1.7292 | 5.465 | 19.05 | 6.4133 | 0.80672 | 1.383 | Y | 1 | 1 | -0.041817 |  | 0.84854 | 0.57488 | 1.1222 | 0.27366 | 1.8778
Square D 2002 | 26 | L | Box | 0.4 | 1.7292 | 5.465 | 19.05 | 8.162 | 0.91113 | 1.383 | Y | 1 | 1 | 0.062599 |  | 0.84854 | 0.57488 | 1.1222 | 0.27366 | 1.8778
Square D 2002 | 27 | L | Box | 0.4 | 1.7292 | 5.465 | 19.05 | 4.4742 | 0.63634 | 1.383 | Y | 1 | 1 | -0.2122 |  | 0.84854 | 0.57488 | 1.1222 | 0.27366 | 1.8778
Square D 2002 | 28 | L | Box | 0.4 | 1.7292 | 5.465 | 19.05 | 4.7727 | 0.53477 | 1.383 | N | 1 | 0 | -0.42691 |  | 0.96168 | 0.68913 | 1.2342 | 0.27255 | 1.873
Square D 2002 | 29 | L | Box | 0.485 | 1.7207 | 5.465 | 19.05 | 8.4647 | 0.9271 | 1.4659 | N | 1 | 0 | -0.12415 |  | 1.0513 | 0.77829 | 1.3242 | 0.27296 | 1.8748
Square D 2002 | 30 | L | Box | 0.4 | 1.7339 | 5.797 | 19.05 | 4.055 | 0.784 | 1.3869 | Y | 1 | 1 | -0.06871 |  | 0.85271 | 0.57903 | 1.1264 | 0.27368 | 1.8779
Square D 2002 | 31 | L | Box | 0.4 | 1.7292 | 5.465 | 31.75 | 5.5713 | 0.74586 | 1.3229 | Y | 1 | 1 | -0.051565 |  | 0.79743 | 0.52382 | 1.071 | 0.27361 | 1.8776
Square D 2002 | 32 | L | Box | 0.4 | 2.0143 | 5.465 | 31.75 | 7.851 | 0.89479 | 1.5478 | Y | 1 | 1 | -0.14578 |  | 1.0406 | 0.76561 | 1.3155 | 0.27496 | 1.8835
Square D 2002 | 33 | L | Box | 0.6 | 2.0026 | 5.167 | 31.75 | 24.3175 | 1.3859 | 1.7816 | Y | 1 | 1 | 0.092468 |  | 1.2934 | 1.0163 | 1.5706 | 0.27718 | 1.8931
Square D 2002 | 34 | L | Box | 0.4 | 2.0143 | 5.465 | 12.7 | 10.3545 | 1.0098 | 1.6545 | Y | 1 | 1 | -0.12528 |  | 1.1351 | 0.85962 | 1.4106 | 0.27548 | 1.8857
Square D 2002 | 35 | L | Box | 0.405 | 0.40671 | 1.878 | 31.75 | 0.207 | -0.73066 | 0.28119 | Y | 1 | 1 | -0.40176 |  | -0.3289 | -0.60656 | -0.05124 | 0.27766 | 1.8952
Square D 2002 | 36 | L | Box | 0.6107 | 0.45429 | 1.93 | 31.75 | 0.6203 | -0.22626 | 0.39093 | N | 1 | 0 | -0.12915 |  | -0.09711 | -0.3721 | 0.17788 | 0.27499 | 1.8836
Square D 2002 | 37 | L | Box | 0.603 | 0.48615 | 0.776 | 31.75 | 0.8137 | -0.09029 | 0.41699 | N | 1 | 0 | -0.021365 |  | -0.06893 | -0.34364 | 0.20579 | 0.27471 | 1.8824
Square D 2002 | 38 | L | Box | 0.606 | 0.45102 | 1.93 | 19.05 | 0.6753 | -0.17087 | 0.39708 | Y | 1 | 1 | 0.046649 |  | -0.21751 | -0.49408 | 0.05905 | 0.27657 | 1.8905
Square D 2002 | 39 | L | Box | 0.405 | 0.40671 | 0.567 | 7.112 | 0.3047 | -0.51926 | 0.29872 | Y | 1 | 1 | -0.1823 |  | -0.33695 | -0.61517 | -0.05874 | 0.27821 | 1.8976
Square D 2002 | 40 | L | Box | 0.609 | 0.45621 | 1.985 | 7.112 | 0.3147 | -0.50377 | 0.41333 | Y | 1 | 1 | -0.29074 |  | -0.21304 | -0.48992 | 0.06385 | 0.27688 | 1.8918
Square D 2002 | 41 | L | Box | 0.4 | 2.0143 | 5.465 | 7.112 | 13.7233 | 1.1371 | 1.6858 | Y | 1 | 1 | -0.025764 |  | 1.1628 | 0.88703 | 1.4386 | 0.27579 | 1.8871
KEMA 2001 | 42 | L | Open | 0.45 | 1.9009 | 10.75 | 38.1 | 10.7253 | 1.0296 | 1.4263 | N | 0 | 0 | 0.23755 |  | 0.79203 | 0.51813 | 1.0659 | 0.2739 | 1.8789
Kinectrics 2400 | 43 | H | Box | 2.382 | 0.41111 | * | 102 | 0.6608 | -0.18139 | 0.40816 | N | 1 | 0 | -0.17993 |  | -0.00146 | -0.27727 | 0.27435 | 0.27581 | 1.8872
Kinectrics 2400 | 44 | H | Box | 2.3768 | 0.6878 | * | 102 | 1.2208 | 0.08627 | 0.68014 | N | 1 | 0 | -0.20634 |  | 0.29262 | 0.01843 | 0.5668 | 0.27419 | 1.8801
Kinectrics 2400 | 45 | H | Box | 2.3738 | 0.84217 | * | 102 | 1.8592 | 0.26914 | 0.83189 | N | 1 | 0 | -0.18756 |  | 0.4567 | 0.18292 | 0.73048 | 0.27378 | 1.8784
Kinectrics 2400 | 46 | H | Box | 2.372 | 1.0658 | * | 102 | 3.1603 | 0.49962 | 1.0518 | N | 1 | 0 | -0.19481 |  | 0.69443 | 0.4206 | 0.96826 | 0.27383 | 1.8786
Kinectrics 2400 | 47 | H | Box | 2.3718 | 0.74687 | * | 102 | 1.7995 | 0.25446 | 0.73821 | N | 1 | 0 | -0.10094 |  | 0.3554 | 0.08142 | 0.62939 | 0.27399 | 1.8793
Kinectrics 2400 | 48 | H | Box | 2.3788 | 1.1619 | * | 102 | 3.8707 | 0.5866 | 1.1462 | N | 1 | 0 | -0.20991 |  | 0.79651 | 0.52242 | 1.0706 | 0.27408 | 1.8797
Kinectrics 2400 | 49 | H | Box | 2.3377 | 1.2098 | * | 102 | 4.6253 | 0.6648 | 1.1933 | N | 1 | 0 | -0.18262 |  | 0.84742 | 0.57316 | 1.1217 | 0.27426 | 1.8804
Kinectrics 2400 | 50 | H | Box | 2.3738 | 1.0658 | * | 102 | 4.6718 | 0.66777 | 1.0518 | N | 1 | 0 | -0.026659 |  | 0.69443 | 0.4206 | 0.96826 | 0.27383 | 1.8786
Kinectrics 2400 | 51 | H | Box | 2.332 | 0.83315 | * | 102 | 3.3847 | 0.52925 | 0.82302 | N | 1 | 0 | 0.082145 |  | 0.44711 | 0.17331 | 0.7209 | 0.27379 | 1.8784
Kinectrics 2400 | 52 | H | Box | 2.3348 | 0.68006 | * | 102 | 2.5788 | 0.41124 | 0.67254 | N | 1 | 0 | 0.12684 |  | 0.2844 | 0.01018 | 0.55861 | 0.27421 | 1.8802
Kinectrics 2400 | 53 | H | Box | 2.345 | 0.40261 | * | 102 | 1.3115 | 0.11583 | 0.39979 | N | 1 | 0 | 0.12634 |  | -0.01051 | -0.28638 | 0.26537 | 0.27588 | 1.8875
Kinectrics 2400 | 54 | H | Box | 2.3598 | 1.2149 | * | 102 | 5.4972 | 0.73991 | 1.1983 | N | 1 | 0 | -0.11297 |  | 0.85289 | 0.57861 | 1.1272 | 0.27428 | 1.8805
Kinectrics 2400 | 55 | H | Box | 2.3693 | 1.1584 | * | 102 | 5.7083 | 0.75541 | 1.1427 | N | 1 | 0 | -0.037359 |  | 0.79277 | 0.5187 | 1.0668 | 0.27407 | 1.8796
Kinectrics 2400 | 57 | H | Box | 2.344 | 1.1761 | * | 102 | 5.3342 | 0.7239 | 1.1601 | N | 1 | 0 | -0.087709 |  | 0.81161 | 0.53748 | 1.0857 | 0.27413 | 1.8799
KEMA 2001 | 58 | H | Open | 4.16 | 0.7356 | 47.383 | 102 | 1.0646 | 0.02401 | 0.72713 | N | 0 | 0 | -0.082058 |  | 0.10606 | -0.16934 | 0.38146 | 0.2754 | 1.8854
KEMA 2001 | 59 | H | Open | 4.16 | 0.78604 | 43.092 | 102 | 1.1802 | 0.07019 | 0.77671 | N | 0 | 0 | -0.089488 |  | 0.15968 | -0.1154 | 0.43475 | 0.27508 | 1.884
KEMA 2001 | 60 | H | Open | 4.16 | 0.99769 | * | 102 | 2.8407 | 0.45166 | 0.98477 | N | 0 | 0 | 0.067027 |  | 0.38464 | 0.1105 | 0.65877 | 0.27413 | 1.8799
KEMA 2001 | 61 | H | Open | 4.16 | 1.2974 | 36.35 | 102 | 6.3 | 0.79893 | 1.2794 | N | 0 | 0 | 0.095755 |  | 0.70318 | 0.42922 | 0.97713 | 0.27395 | 1.8791
KEMA 2001 | 62 | H | Open | 4.16 | 1.6067 | 25.106 | 102 | 15.9225 | 1.202 | 1.5835 | N | 0 | 0 | 0.17003 |  | 1.032 | 0.75679 | 1.3072 | 0.27519 | 1.8845
KEMA 2001 | 63 | H | Open | 4.16 | 1.2974 | 36.35 | 102 | 6.1714 | 0.78877 | 1.2794 | N | 0 | 0 | 0.08559 |  | 0.70318 | 0.42922 | 0.97713 | 0.27395 | 1.8791
KEMA 2001 | 64 | H | Open | 13.8 | 0.75664 | 81.295 | 152 | 1.6952 | 0.22898 | 0.74781 | N | 0 | 0 | 0.045746 |  | 0.18324 | -0.09733 | 0.4638 | 0.28057 | 1.9079
KEMA 2001 | 65 | H | Open | 13.8 | 1 | 89.28 | 152 | 2.9602 | 0.47126 | 0.98704 | N | 0 | 0 | 0.02936 |  | 0.4419 | 0.16206 | 0.72175 | 0.27985 | 1.9048
KEMA 2001 | 66 | H | Open | 13.8 | 1.3032 | 51.011 | 152 | 5.7848 | 0.75675 | 1.2851 | N | 0 | 0 | -0.007414 |  | 0.76416 | 0.48398 | 1.0443 | 0.28018 | 1.9062
KEMA 2001 | 67 | H | Open | 13.8 | 1.6107 | 33.769 | 152 | 15.7488 | 1.197 | 1.5873 | N | 0 | 0 | 0.106 |  | 1.091 | 0.80906 | 1.3728 | 0.2819 | 1.9138
KEMA 2001 | 68 | H | Open | 13.8 | 1.3032 | 51.011 | 152 | 7.0986 | 0.84686 | 1.2851 | N | 0 | 0 | 0.082694 |  | 0.76416 | 0.48398 | 1.0443 | 0.28018 | 1.9062
KEMA 2001 | 69 | H | Open | 13.8 | 1.3032 | 51.011 | 13 | 1.8492 | 0.26056 | 1.2851 | N | 0 | 0 | -0.35122 |  | 0.61178 | 0.33565 | 0.88791 | 0.27613 | 1.8886
Paper 97-35 | 70 | L | Open | 0.61 | 1.5593 | * | 19.1 | 3.918 | 0.59306 | 1.3889 | N | 0 | 0 | -0.13767 |  | 0.73073 | 0.45531 | 1.0062 | 0.27542 | 1.8855
Paper 97-35 | 71 | L | Open | 0.61 | 1.5593 | * | 25.4 | 3.683 | 0.5662 | 1.3623 | N | 0 | 0 | -0.1427 |  | 0.7089 | 0.43411 | 0.9837 | 0.27479 | 1.8828
Paper 97-35 | 72 | L | Open | 0.61 | 1.5593 | * | 31.8 | 4.258 | 0.62921 | 1.3353 | N | 0 | 0 | -0.057522 |  | 0.68673 | 0.41248 | 0.96097 | 0.27424 | 1.8804
Paper 97-35 | 73 | L | Open | 0.61 | 1.5593 | * | 50.8 | 3.709 | 0.56926 | 1.2552 | N | 0 | 0 | -0.051635 |  | 0.62089 | 0.34776 | 0.89402 | 0.27313 | 1.8756
Paper 97-35 | 74 | L | Open | 0.61 | 1.5593 | * | 76.2 | 2.377 | 0.37603 | 1.148 | N | 0 | 0 | -0.15685 |  | 0.53288 | 0.26003 | 0.80573 | 0.27285 | 1.8743
Paper 97-35 | 75 | L |  | 0.61 | 1.5593 | * | 19.1 | 3.474 | 0.54083 | 1.4455 | N | * | 0 | * |  | * | * | * | * | *
Paper 97-35 | 76 | L |  | 0.61 | 1.5593 | * | 25.4 | 4.388 | 0.64227 | 1.4189 | N | * | 0 | * |  | * | * | * | * | *
Paper 97-35 | 77 | L |  | 0.61 | 1.5593 | * | 31.8 | 4.493 | 0.65254 | 1.3919 | N | * | 0 | * |  | * | * | * | * | *
Paper 97-35 | 78 | L | Box | 0.61 | 1.5593 | * | 31.8 | 13.559 | 1.1322 | 1.3919 | N | 1 | 0 | 0.147 |  | 0.98523 | 0.71318 | 1.2573 | 0.27205 | 1.8709
Paper Vol 36-1 | 79 | L | Open | 0.768 | 1.7023 | * | 32 | 9.26 | 0.96661 | 1.6296 | N | 0 | 0 | -0.038459 |  | 1.0051 | 0.7301 | 1.28 | 0.27497 | 1.8835
Paper Vol 36-1 | 80 | L | Open | 0.687 | 1.6567 | * | 32 | 7.74 | 0.88874 | 1.5014 | N | 0 | 0 | 0.022274 |  | 0.86647 | 0.59199 | 1.1409 | 0.27448 | 1.8814
Paper Vol 36-1 | 81 | L | Open | 0.614 | 1.6119 | * | 32 | 5.92 | 0.77232 | 1.3861 | N | 0 | 0 | 0.03045 |  | 0.74187 | 0.46761 | 1.0161 | 0.27426 | 1.8804
Paper Vol 36-1 | 82 | L | Open | 0.616 | 1.5476 | * | 32 | 5.04 | 0.70243 | 1.3297 | N | 0 | 0 | 0.021571 |  | 0.68086 | 0.40663 | 0.95509 | 0.27423 | 1.8803
Paper Vol 36-1 | 83 | L | Open | 0.623 | 1.4936 | * | 32 | 4.6 | 0.66276 | 1.2871 | N | 0 | 0 | 0.027968 |  | 0.63479 | 0.36055 | 0.90903 | 0.27424 | 1.8803
Paper Vol 36-1 | 84 | L | Open | 0.617 | 1.4419 | * | 32 | 3.94 | 0.5955 | 1.2345 | N | 0 | 0 | 0.017626 |  | 0.57787 | 0.30358 | 0.85216 | 0.27429 | 1.8806
Paper Vol 36-1 | 85 | L | Open | 0.614 | 1.3694 | * | 32 | 3.56 | 0.55145 | 1.166 | N | 0 | 0 | 0.047613 |  | 0.50384 | 0.22942 | 0.77825 | 0.27442 | 1.8811
Paper Vol 36-1 | 86 | L | Open | 0.615 | 1.2806 | * | 32 | 2.5 | 0.39794 | 1.0862 | N | 0 | 0 | -0.0196 |  | 0.41754 | 0.14288 | 0.6922 | 0.27466 | 1.8822
Paper Vol 36-1 | 87 | L | Open | 0.616 | 1.2122 | * | 32 | 2.2 | 0.34242 | 1.0248 | N | 0 | 0 | -0.00879 |  | 0.35121 | 0.0763 | 0.62613 | 0.27492 | 1.8833
Paper Vol 36-1 | 88 | L | Box | 0.759 | 1.7092 | * | 32 | 24.92 | 1.3965 | 1.6834 | N | 1 | 0 | 0.095859 |  | 1.3007 | 1.0266 | 1.5748 | 0.27414 | 1.8799
Paper Vol 36-1 | 89 | L | Box | 0.68 | 1.6632 | * | 32 | 19.7 | 1.2945 | 1.557 | N | 1 | 0 | 0.13054 |  | 1.1639 | 0.89086 | 1.437 | 0.27307 | 1.8753
Paper Vol 36-1 | 90 | L | Box | 0.612 | 1.6232 | * | 32 | 16.02 | 1.2047 | 1.4508 | N | 1 | 0 | 0.15546 |  | 1.0492 | 0.77685 | 1.3216 | 0.27236 | 1.8722
Paper Vol 36-1 | 91 | L | Box | 0.618 | 1.5593 | * | 32 | 10.8 | 1.0334 | 1.3988 | N | 1 | 0 | 0.040515 |  | 0.99291 | 0.72083 | 1.265 | 0.27208 | 1.871
Paper Vol 36-1 | 92 | L | Box | 0.613 | 1.4942 | * | 32 | 8.02 | 0.90417 | 1.3348 | N | 1 | 0 | -0.019597 |  | 0.92377 | 0.65199 | 1.1956 | 0.27178 | 1.8698
Paper Vol 36-1 | 93 | L | Box | 0.617 | 1.4419 | * | 32 | 7.26 | 0.86094 | 1.291 | N | 1 | 0 | -0.015436 |  | 0.87637 | 0.60475 | 1.148 | 0.27162 | 1.8691
Paper Vol 36-1 | 94 | L | Box | 0.611 | 1.3738 | * | 32 | 5.92 | 0.77232 | 1.224 | N | 1 | 0 | -0.031562 |  | 0.80388 | 0.53245 | 1.0753 | 0.27143 | 1.8682
Paper Vol 36-1 | 95 | L | Box | 0.615 | 1.2806 | * | 32 | 6.2 | 0.79239 | 1.1427 | N | 1 | 0 | 0.076349 |  | 0.71604 | 0.44474 | 0.98734 | 0.2713 | 1.8677
Paper Vol 36-1 | 96 | L | Box | 0.616 | 1.2122 | * | 32 | 5.1 | 0.70757 | 1.0814 | N | 1 | 0 | 0.057854 |  | 0.64972 | 0.37845 | 0.92098 | 0.27127 | 1.8675
CLF Paper | 97 | L | Box | 0.6 | 2.0253 | 7.9 | 32 | 43.037 | 1.6338 | 1.8007 | N | 1 | 0 | 0.20636 |  | 1.4275 | 1.1521 | 1.7028 | 0.27536 | 1.8852
CLF Paper | 98 | L | Box | 0.6 | 1.8189 | 9.95 | 32 | 25.658 | 1.4092 | 1.615 | N | 1 | 0 | 0.18258 |  | 1.2266 | 0.95311 | 1.5002 | 0.27353 | 1.8773
CLF Paper | 99 | L | Box | 0.6 | 1.6444 | 11 | 32 | 18.897 | 1.2764 | 1.458 | N | 1 | 0 | 0.21949 |  | 1.0569 | 0.7845 | 1.3293 | 0.2724 | 1.8724
CLF Paper | 100 | L | Box | 0.6 | 1.3541 | 4.9 | 32 | 9.388 | 0.97257 | 1.1967 | N | 1 | 0 | 0.19816 |  | 0.77442 | 0.50304 | 1.0458 | 0.27138 | 1.868
Kinectrics 2001 | 101 | L | Box | 0.405 | 1.0531 | 10 | 25 | 2.449 | 0.38899 | 0.81099 | N | 1 | 0 | 0.039301 |  | 0.34969 | 0.07747 | 0.62191 | 0.27222 | 1.8716
Square D 2002 | 102 | L | Box | 0.606 | 1.3514 | 5.465 | 38.1 | 3.239 | 0.51041 | 1.1775 | Y | 1 | 1 | -0.13679 |  | 0.6472 | 0.37384 | 0.92056 | 0.27336 | 1.8765
Square D 2002 | 103 | L | Box | 0.208 | 1.942 | 6.169 | 12.7 | 3.124 | 0.49471 | 1.3664 | Y | 1 | 1 | -0.3289 |  | 0.82361 | 0.55001 | 1.0972 | 0.2736 | 1.8776
Square D 2002 | 104 | L | Box | 0.606 | 2.0069 | 5.167 | 7.112 | 22.113 | 1.3446 | 1.9303 | Y | 1 | 1 | -0.082565 |  | 1.4272 | 1.1488 | 1.7057 | 0.27844 | 1.8986

## Arc Current Model - LV Data
Data set used for Minitab Analysis of Data - IEEE 1584 Working Group
Arc Current equation analysis - under 5kV
|  | kV |  |  | kA |  |  | mm | mm | mm | mm | kA
RepGrp | Test Set | Voltage OC | VoltClass | Open/Box | Ibf | Log(Ibf) | X/R | ElectrGap | BoxGap | BoxW+H | BoxD | Iarc | Log(Iarc) | IncidEmax_norm | RESI4 | COEF4 | RESI1 | COEF1 | FITS1
97 | CLF Paper | 0.6 | L | Box | 106 | 2.0253 | 7.9 | 32 | 102 | 508 | 508 | 45.98 | 1.6626 | 43.037 | -0.13814 | -0.12488 | -0.13814 | -0.12488 | 1.8007
98 | CLF Paper | 0.6 | L | Box | 65.9 | 1.8189 | 9.95 | 32 | 102 | 508 | 508 | 36.77 | 1.5655 | 25.658 | -0.04946 | 0.028274 | -0.04946 | 0.028274 | 1.615
99 | CLF Paper | 0.6 | L | Box | 44.1 | 1.6444 | 11 | 32 | 102 | 508 | 508 | 25.97 | 1.4145 | 18.897 | -0.0435 | 0.662 | -0.0435 | 0.662 | 1.458
100 | CLF Paper | 0.6 | L | Box | 22.6 | 1.3541 | 4.9 | 32 | 102 | 508 | 508 | 15.8 | 1.1987 | 9.388 | 0.001948 | 0.096571 | 0.001948 | 0.096571 | 1.1967
42 | KEMA 2001 | 0.45 | L | Open | 79.6 | 1.9009 | 10.75 | 38.1 | 10000 | 10000 | 10000 | 21.9333 | 1.3361 | 10.7253 | -0.090185 | 0.55876 | -0.090185 | 0.55876 | 1.4263
3 | Kinectrics 2001 | 0.6 | L | Box | 0.671 | -0.17328 | 40 | 32 | 102 | 508 | 508 | 0.6138 | -0.21204 | 0.1192 | -0.034281 | 0.000526 | -0.034281 | 0.000526 | -0.17776
4 | Kinectrics 2001 | 0.6 | L | Box | 3.478 | 0.54133 | 25 | 32 | 102 | 508 | 508 | 3.0223 | 0.48033 | 1.9307 | 0.015024 | -0.003043 | 0.015024 | -0.003043 | 0.4653
5 | Kinectrics 2001 | 0.59 | L | Box | 3.35 | 0.52504 | 25 | 10 | 10 | 508 | 508 | 3.1447 | 0.49757 | 1.7307 | 0.02725 |  | 0.02725 |  | 0.47032
6 | Kinectrics 2001 | 0.59 | L | Box | 3.35 | 0.52504 | 25 | 40 | 10 | 508 | 508 | 2.8263 | 0.45122 | 1.561 | 0.013045 |  | 0.013045 |  | 0.43818
7 | Kinectrics 2001 | 0.59 | L | Box | 3.35 | 0.52504 | 25 | 40 | 102 | 508 | 508 | 2.5707 | 0.41004 | 1.446 | -0.028141 |  | -0.028141 |  | 0.43818
8 | Kinectrics 2001 | 0.59 | L | Box | 3.35 | 0.52504 | 25 | 10 | 102 | 508 | 508 | 3.1623 | 0.50001 | 1.147 | 0.029682 |  | 0.029682 |  | 0.47032
9 | Kinectrics 2001 | 0.59 | L | Box | 30 | 1.4771 | 6.5 | 10 | 102 | 508 | 508 | 24.3287 | 1.3861 | 6.6333 | 0.000597 |  | 0.000597 |  | 1.3855
10 | Kinectrics 2001 | 0.59 | L | Box | 30 | 1.4771 | 6.5 | 40 | 102 | 508 | 508 | 21.307 | 1.3285 | 6.736 | 0.062055 |  | 0.062055 |  | 1.2664
11 | Kinectrics 2001 | 0.59 | L | Box | 30 | 1.4771 | 6.5 | 10 | 102 | 508 | 508 | 24.568 | 1.3904 | 5.78 | 0.004874 |  | 0.004874 |  | 1.3855
12 | Kinectrics 2001 | 0.59 | L | Box | 30 | 1.4771 | 6.5 | 10 | 10 | 508 | 508 | 24.546 | 1.39 | 9.7977 | 0.004466 |  | 0.004466 |  | 1.3855
13 | Kinectrics 2001 | 0.59 | L | Box | 30 | 1.4771 | 6.5 | 40 | 10 | 508 | 508 | 22.094 | 1.3442 | 10.388 | 0.077812 |  | 0.077812 |  | 1.2664
14 | Kinectrics 2001 | 0.25 | L | Box | 20 | 1.301 | 7 | 10 | 10 | 508 | 508 | 12.596 | 1.0995 | 3.3816 | 0.16322 |  | 0.16322 |  | 0.93623
15 | Kinectrics 2001 | 0.405 | L | Box | 11.3 | 1.0531 | 10 | 25 | 56 | 508 | 508 | 4.469 | 0.64994 | 2.568 | -0.16106 |  | -0.16106 |  | 0.81099
16 | Kinectrics 2001 | 0.59 | L | Box | 2.7 | 0.43136 | 30 | 10 | 10 | 508 | 508 | 2.5517 | 0.4068 | 0.9597 | 0.02653 |  | 0.02653 |  | 0.38027
17 | Kinectrics 2001 | 0.59 | L | Box | 2.7 | 0.43136 | 30 | 40 | 10 | 508 | 508 | 2.3963 | 0.37954 | 1.0233 | 0.022863 |  | 0.022863 |  | 0.35668
18 | Kinectrics 2001 | 0.59 | L | Box | 2.7 | 0.43136 | 30 | 40 | 102 | 508 | 508 | 2.3155 | 0.36454 | 0.8982 | 0.007862 |  | 0.007862 |  | 0.35668
19 | Kinectrics 2001 | 0.59 | L | Box | 2.7 | 0.43136 | 30 | 10 | 102 | 508 | 508 | 2.5617 | 0.40851 | 0.688 | 0.028238 |  | 0.028238 |  | 0.38027
20 | Kinectrics 2001 | 0.59 | L | Box | 21.4 | 1.3304 | 7 | 10 | 102 | 508 | 508 | 18.9327 | 1.2772 | 4.135 | 0.032734 |  | 0.032734 |  | 1.2445
21 | Kinectrics 2001 | 0.59 | L | Box | 21.4 | 1.3304 | 7 | 40 | 102 | 508 | 508 | 16.7017 | 1.2227 | 5.5183 | 0.083922 |  | 0.083922 |  | 1.1388
22 | Kinectrics 2001 | 0.59 | L | Box | 21.4 | 1.3304 | 7 | 40 | 10 | 508 | 508 | 17.3977 | 1.2405 | 8.2463 | 0.10168 |  | 0.10168 |  | 1.1388
23 | Kinectrics 2001 | 0.59 | L | Box | 21.4 | 1.3304 | 7 | 10 | 10 | 508 | 508 | 19.079 | 1.2805 | 7.163 | 0.036062 |  | 0.036062 |  | 1.2445
101 | Kinectrics 2001 | 0.405 | L | Box | 11.3 | 1.0531 | 10 | 25 | 56 | 508 | 508 | 5.451 | 0.73648 | 2.449 | -0.074515 |  | -0.074515 |  | 0.81099
70 | Paper 97-35 | 0.61 | L | Open | 36.25 | 1.5593 | * | 19.1 | 10000 | 10000 | 10000 | 25.52 | 1.4069 | 3.918 | 0.017965 |  | 0.017965 |  | 1.3889
71 | Paper 97-35 | 0.61 | L | Open | 36.25 | 1.5593 | * | 25.4 | 10000 | 10000 | 10000 | 24.23 | 1.3843 | 3.683 | 0.022015 |  | 0.022015 |  | 1.3623
72 | Paper 97-35 | 0.61 | L | Open | 36.25 | 1.5593 | * | 31.8 | 10000 | 10000 | 10000 | 22.12 | 1.3448 | 4.258 | 0.009446 |  | 0.009446 |  | 1.3353
73 | Paper 97-35 | 0.61 | L | Open | 36.25 | 1.5593 | * | 50.8 | 10000 | 10000 | 10000 | 17.79 | 1.2502 | 3.709 | -0.00501 |  | -0.00501 |  | 1.2552
74 | Paper 97-35 | 0.61 | L | Open | 36.25 | 1.5593 | * | 76.2 | 10000 | 10000 | 10000 | 11.76 | 1.0704 | 2.377 | -0.077626 |  | -0.077626 |  | 1.148
75 | Paper 97-35 | 0.61 | L | Box | 36.25 | 1.5593 | * | 19.1 | 102 | 10000 | 10000 | 24.9 | 1.3962 | 3.474 | -0.049263 |  | -0.049263 |  | 1.4455
76 | Paper 97-35 | 0.61 | L | Box | 36.25 | 1.5593 | * | 25.4 | 102 | 10000 | 10000 | 24.67 | 1.3922 | 4.388 | -0.026716 |  | -0.026716 |  | 1.4189
77 | Paper 97-35 | 0.61 | L | Box | 36.25 | 1.5593 | * | 31.8 | 102 | 10000 | 10000 | 22.82 | 1.3583 | 4.493 | -0.033571 |  | -0.033571 |  | 1.3919
78 | Paper 97-35 | 0.61 | L | Box | 36.25 | 1.5593 | * | 31.8 | 102 | 533 | 533 | 28.67 | 1.4574 | 13.559 | 0.065541 |  | 0.065541 |  | 1.3919
1 | Paper Vol 36-1 | 0.614 | L | Open | 40.92 | 1.6119 | * | 32 | 10000 | 10000 | 10000 | 25.455 | 1.4058 | 6.2815 | 0.019636 |  | 0.019636 |  | 1.3861
2 | Paper Vol 36-1 | 0.612 | L | Box | 41.99 | 1.6232 | * | 32 | 102 | 508 | 508 | 31.916 | 1.504 | 16.3348 | 0.053135 |  | 0.053135 |  | 1.4508
79 | Paper Vol 36-1 | 0.768 | L | Open | 50.39 | 1.7023 | * | 32 | 10000 | 10000 | 10000 | 34.88 | 1.5426 | 9.26 | -0.086983 |  | -0.086983 |  | 1.6296
80 | Paper Vol 36-1 | 0.687 | L | Open | 45.36 | 1.6567 | * | 32 | 10000 | 10000 | 10000 | 30.15 | 1.4793 | 7.74 | -0.022083 |  | -0.022083 |  | 1.5014
81 | Paper Vol 36-1 | 0.614 | L | Open | 40.92 | 1.6119 | * | 32 | 10000 | 10000 | 10000 | 24.08 | 1.3817 | 5.92 | -0.004481 |  | -0.004481 |  | 1.3861
82 | Paper Vol 36-1 | 0.616 | L | Open | 35.29 | 1.5476 | * | 32 | 10000 | 10000 | 10000 | 22.3 | 1.3483 | 5.04 | 0.018596 |  | 0.018596 |  | 1.3297
83 | Paper Vol 36-1 | 0.623 | L | Open | 31.16 | 1.4936 | * | 32 | 10000 | 10000 | 10000 | 20.99 | 1.322 | 4.6 | 0.034911 |  | 0.034911 |  | 1.2871
84 | Paper Vol 36-1 | 0.617 | L | Open | 27.66 | 1.4419 | * | 32 | 10000 | 10000 | 10000 | 18.74 | 1.2728 | 3.94 | 0.038311 |  | 0.038311 |  | 1.2345
85 | Paper Vol 36-1 | 0.614 | L | Open | 23.41 | 1.3694 | * | 32 | 10000 | 10000 | 10000 | 16.44 | 1.2159 | 3.56 | 0.049914 |  | 0.049914 |  | 1.166
86 | Paper Vol 36-1 | 0.615 | L | Open | 19.08 | 1.2806 | * | 32 | 10000 | 10000 | 10000 | 13.27 | 1.1229 | 2.5 | 0.036696 |  | 0.036696 |  | 1.0862
87 | Paper Vol 36-1 | 0.616 | L | Open | 16.3 | 1.2122 | * | 32 | 10000 | 10000 | 10000 | 11.58 | 1.0637 | 2.2 | 0.038877 |  | 0.038877 |  | 1.0248
88 | Paper Vol 36-1 | 0.759 | L | Box | 51.19 | 1.7092 | * | 32 | 102 | 508 | 508 | 41.15 | 1.6144 | 24.92 | -0.06907 |  | -0.06907 |  | 1.6834
89 | Paper Vol 36-1 | 0.68 | L | Box | 46.05 | 1.6632 | * | 32 | 102 | 508 | 508 | 36.33 | 1.5603 | 19.7 | 0.00331 |  | 0.00331 |  | 1.557
90 | Paper Vol 36-1 | 0.612 | L | Box | 41.99 | 1.6232 | * | 32 | 102 | 508 | 508 | 31.59 | 1.4995 | 16.02 | 0.048697 |  | 0.048697 |  | 1.4508
91 | Paper Vol 36-1 | 0.618 | L | Box | 36.25 | 1.5593 | * | 32 | 102 | 508 | 508 | 27.31 | 1.4363 | 10.8 | 0.037536 |  | 0.037536 |  | 1.3988
92 | Paper Vol 36-1 | 0.613 | L | Box | 31.2 | 1.4942 | * | 32 | 102 | 508 | 508 | 24.92 | 1.3965 | 8.02 | 0.061706 |  | 0.061706 |  | 1.3348
93 | Paper Vol 36-1 | 0.617 | L | Box | 27.66 | 1.4419 | * | 32 | 102 | 508 | 508 | 21.9 | 1.3404 | 7.26 | 0.049439 |  | 0.049439 |  | 1.291
94 | Paper Vol 36-1 | 0.611 | L | Box | 23.65 | 1.3738 | * | 32 | 102 | 508 | 508 | 19.01 | 1.279 | 5.92 | 0.055019 |  | 0.055019 |  | 1.224
95 | Paper Vol 36-1 | 0.615 | L | Box | 19.08 | 1.2806 | * | 32 | 102 | 508 | 508 | 15.57 | 1.1923 | 6.2 | 0.049567 |  | 0.049567 |  | 1.1427
96 | Paper Vol 36-1 | 0.616 | L | Box | 16.3 | 1.2122 | * | 32 | 102 | 508 | 508 | 13.24 | 1.1219 | 5.1 | 0.040509 |  | 0.040509 |  | 1.0814
24 | Square D 2002 | 0.6 | L | Box | 22.238 | 1.3471 | 5.465 | 38.1 | 38 | 330 | 191 | 16.008 | 1.2043 | 4.3615 | 0.035733 |  | 0.035733 |  | 1.1686
25 | Square D 2002 | 0.4 | L | Box | 53.607 | 1.7292 | 5.465 | 19.05 | 38 | 330 | 191 | 25.206 | 1.4005 | 6.4133 | 0.017471 |  | 0.017471 |  | 1.383
26 | Square D 2002 | 0.4 | L | Box | 53.607 | 1.7292 | 5.465 | 19.05 | 38 | 330 | 191 | 25.0053 | 1.3975 | 8.162 | 0.014481 |  | 0.014481 |  | 1.383
27 | Square D 2002 | 0.4 | L | Box | 53.607 | 1.7292 | 5.465 | 19.05 | 38 | 330 | 191 | 27.0626 | 1.4313 | 5.714 | 0.048234 |  | 0.048234 |  | 1.383
28 | Square D 2002 | 0.4 | L | Box | 53.607 | 1.7292 | 5.465 | 19.05 | 38 | 330 | 191 | 26.69 | 1.4261 | 4.7727 | 0.043014 |  | 0.043014 |  | 1.383
29 | Square D 2002 | 0.485 | L | Box | 52.56 | 1.7207 | 5.465 | 19.05 | 38 | 330 | 191 | 30.9667 | 1.4909 | 8.4647 | 0.025018 |  | 0.025018 |  | 1.4659
30 | Square D 2002 | 0.4 | L | Box | 54.186 | 1.7339 | 5.797 | 19.05 | 38 | 330 | 191 | 25.35 | 1.4039 | 6.0825 | 0.017048 |  | 0.017048 |  | 1.3869
31 | Square D 2002 | 0.4 | L | Box | 53.607 | 1.7292 | 5.465 | 31.75 | 38 | 330 | 191 | 22.3847 | 1.349 | 5.5713 | 0.026087 |  | 0.026087 |  | 1.3229
32 | Square D 2002 | 0.4 | L | Box | 103.34 | 2.0143 | 5.465 | 31.75 | 38 | 330 | 191 | 27.6033 | 1.4408 | 7.851 | -0.10697 |  | -0.10697 |  | 1.5478
33 | Square D 2002 | 0.6 | L | Box | 100.594 | 2.0026 | 5.167 | 31.75 | 38 | 330 | 191 | 53.3235 | 1.7268 | 24.3175 | -0.054814 |  | -0.054814 |  | 1.7816
34 | Square D 2002 | 0.4 | L | Box | 103.34 | 2.0143 | 5.465 | 12.7 | 38 | 330 | 191 | 40.235 | 1.6021 | 10.3545 | -0.052431 |  | -0.052431 |  | 1.6545
35 | Square D 2002 | 0.405 | L | Box | 2.551 | 0.40671 | 1.878 | 31.75 | 38 | 330 | 191 | 1.8355 | 0.2584 | 0.207 | -0.022795 |  | -0.022795 |  | 0.28119
36 | Square D 2002 | 0.61067 | L | Box | 2.846 | 0.45429 | 1.93 | 31.75 | 38 | 330 | 191 | 2.0463 | 0.31097 | 0.6203 | -0.079956 |  | -0.079956 |  | 0.39093
37 | Square D 2002 | 0.603 | L | Box | 3.063 | 0.48615 | 0.776 | 31.75 | 38 | 330 | 191 | 1.8947 | 0.27753 | 0.8137 | -0.13946 |  | -0.13946 |  | 0.41699
38 | Square D 2002 | 0.606 | L | Box | 2.825 | 0.45102 | 1.93 | 19.05 | 38 | 330 | 191 | 2.0527 | 0.31232 | 0.6753 | -0.084769 |  | -0.084769 |  | 0.39708
39 | Square D 2002 | 0.405 | L | Box | 2.551 | 0.40671 | 0.567 | 7.112 | 9 | 330 | 191 | 1.8733 | 0.27257 | 0.3047 | -0.026155 |  | -0.026155 |  | 0.29872
40 | Square D 2002 | 0.609 | L | Box | 2.859 | 0.45621 | 1.985 | 7.112 | 9 | 330 | 191 | 2.2003 | 0.34248 | 0.3147 | -0.070846 |  | -0.070846 |  | 0.41333
41 | Square D 2002 | 0.4 | L | Box | 103.34 | 2.0143 | 5.465 | 7.112 | 38 | 330 | 191 | 48.287 | 1.6835 | 13.7233 | -0.002298 |  | -0.002298 |  | 1.6858
102 | Square D 2002 | 0.606 | L | Box | 22.46 | 1.3514 | 5.465 | 38.1 | 38 | 330 | 191 | 18.11 | 1.2579 | 3.239 | 0.080403 |  | 0.080403 |  | 1.1775
103 | Square D 2002 | 0.208 | L | Box | 87.5 | 1.942 | 6.169 | 12.7 | 38 | 330 | 191 | 20.853 | 1.3192 | 3.124 | -0.047252 |  | -0.047252 |  | 1.3664
104 | Square D 2002 | 0.606 | L | Box | 101.6 | 2.0069 | 5.167 | 7.112 | 38 | 330 | 191 | 65.16 | 1.814 | 22.113 | -0.11635 |  | -0.11635 |  | 1.9303

## Arc Current Model - HV Data
Data set used for Minitab Analysis of Data - IEEE 1584 Working Group
Arc Current equation analysis - over 5kV
|  | kV |  |  | kA |  |  | mm | mm | mm | mm | kA
RepGrp | Test Set | Voltage OC | VoltClass | Open/Box | Ibf | Log(Ibf) | X/R | ElectrGap | BoxGap | BoxW+H | BoxD | Iarc | Log(Iarc) | IncidEmax_norm | RESI1 | HI1 | COOK1 | RESI2 | COEF2 | RESI3 | COEF3 | FITS3
58 | KEMA 2001 | 4.16 | H | Open | 5.44 | 0.7356 | 47.383 | 102 | 10000 | 10000 | 10000 | 5.2934 | 0.72372 | 1.0646 | -0.0085812 | 0.26253 | 0.07495 | -0.00745 | 0.073746 | -0.0034101 | 0.004025 | 0.72713
59 | KEMA 2001 | 4.16 | H | Open | 6.11 | 0.78604 | 43.092 | 102 | 10000 | 10000 | 10000 | 5.91 | 0.77157 | 1.1802 | -0.010405 | 0.22303 | 0.08434 | -0.0083224 | -0.001493 | -0.0051425 | 0.98301 | 0.77671
60 | KEMA 2001 | 4.16 | H | Open | 9.947 | 0.99769 | * | 102 | 10000 | 10000 | 10000 | 9.8492 | 0.99337 | 2.8407 | 0.0029522 | 0.11083 | 0.00258 | 0.0090294 | 0.91878 | 0.0086006 |  | 0.98477
61 | KEMA 2001 | 4.16 | H | Open | 19.833 | 1.2974 | 36.35 | 102 | 10000 | 10000 | 10000 | 19.4332 | 1.2868 | 6.3 | 0.0012396 | 0.099875 | 0.0004 | 0.012972 | 0.000764 | 0.0074339 |  | 1.2794
62 | KEMA 2001 | 4.16 | H | Open | 40.433 | 1.6067 | 25.106 | 102 | 10000 | 10000 | 10000 | 36.025 | 1.5544 | 15.9225 | -0.035833 | 0.27042 | 1.3754 | -0.018263 | 0.001175 | -0.029076 |  | 1.5835
63 | KEMA 2001 | 4.16 | H | Open | 19.833 | 1.2974 | 36.35 | 102 | 10000 | 10000 | 10000 | 19.3182 | 1.2859 | 6.1714 | 0.0003616 | 0.099875 | 3e-05 | 0.012094 | -0.000567 | 0.0065558 |  | 1.2794
64 | KEMA 2001 | 13.8 | H | Open | 5.71 | 0.75664 | 81.295 | 152 | 10000 | 10000 | 10000 | 5.6506 | 0.75209 | 1.6688 | -0.0009275 | 0.24546 | 0.00078 | -0.0026861 | 0.000415 | 0.0042818 |  | 0.74781
65 | KEMA 2001 | 13.8 | H | Open | 10 | 1 | 89.28 | 152 | 10000 | 10000 | 10000 | 9.9935 | 0.99971 | 2.9198 | 0.0070228 | 0.11008 | 0.01446 | 0.0020548 |  | 0.012675 |  | 0.98704
66 | KEMA 2001 | 13.8 | H | Open | 20.1 | 1.3032 | 51.011 | 152 | 10000 | 10000 | 10000 | 20.125 | 1.3037 | 5.779 | 0.012445 | 0.10138 | 0.04099 | 0.003478 |  | 0.018649 |  | 1.2851
67 | KEMA 2001 | 13.8 | H | Open | 40.8 | 1.6107 | 33.769 | 152 | 10000 | 10000 | 10000 | 40.2134 | 1.6044 | 15.7238 | 0.010273 | 0.27377 | 0.1155 | -0.0027486 |  | 0.017038 |  | 1.5873
68 | KEMA 2001 | 13.8 | H | Open | 20.1 | 1.3032 | 51.011 | 152 | 10000 | 10000 | 10000 | 19.9583 | 1.3001 | 10.0198 | 0.0088293 | 0.10138 | 0.02063 | -0.0001373 |  | 0.015034 |  | 1.2851
69 | KEMA 2001 | 13.8 | H | Open | 20.1 | 1.3032 | 51.011 | 13 | 10000 | 10000 | 10000 | 20.1334 | 1.3039 | * | 0.012625 | 0.10138 | 0.04219 | -2.2e-05 |  | 0.018829 |  | 1.2851
43 | Kinectrics 2400 | 2.382 | H | Box | 2.577 | 0.41111 | * | 102 | 152 | 953 | 762 | 2.556 | 0.40755 | 0.6608 | -0.0049912 | 0.29796 | 0.03176 | -0.004977 |  | -0.0006089 |  | 0.40816
44 | Kinectrics 2400 | 2.3768 | H | Box | 4.873 | 0.6878 | * | 102 | 152 | 953 | 762 | 4.8108 | 0.68219 | 1.2208 | 0.0029985 | 0.11503 | 0.00278 | 0.0029912 |  | 0.0020555 |  | 0.68014
45 | Kinectrics 2400 | 2.3738 | H | Box | 6.953 | 0.84217 | * | 102 | 152 | 953 | 762 | 6.756 | 0.82968 | 1.8595 | 0.0017072 | 0.074997 | 0.00054 | 0.0016895 |  | -0.0022071 |  | 0.83189
46 | Kinectrics 2400 | 2.372 | H | Box | 11.637 | 1.0658 | * | 102 | 152 | 953 | 762 | 11.0693 | 1.0441 | 3.1605 | 0.0005675 | 0.095839 | 8e-05 | 0.0005313 |  | -0.0076519 |  | 1.0518
47 | Kinectrics 2400 | 2.3718 | H | Box | 5.583 | 0.74687 | * | 102 | 152 | 953 | 762 | 5.61 | 0.7487 | 1.8 | 0.012574 | 0.094459 | 0.0384 | 0.012569 |  | 0.010494 |  | 0.73821
48 | Kinectrics 2400 | 2.3788 | H | Box | 14.517 | 1.1619 | * | 102 | 152 | 953 | 762 | 13.7065 | 1.1369 | 3.871 | 0.0008281 | 0.13341 | 0.00026 | 0.0007684 |  | -0.0092396 |  | 1.1462
49 | Kinectrics 2400 | 2.3377 | H | Box | 16.21 | 1.2098 | * | 102 | 152 | 953 | 762 | 15.21 | 1.1821 | 4.6258 | -0.0001426 | 0.15859 | 1e-05 | -0.0001176 |  | -0.011132 |  | 1.1933
50 | Kinectrics 2400 | 2.3738 | H | Box | 11.637 | 1.0658 | * | 102 | 152 | 953 | 762 | 11.1107 | 1.0457 | 4.6723 | 0.0021944 | 0.095839 | 0.00119 | 0.0021547 |  | -0.0060249 |  | 1.0518
51 | Kinectrics 2400 | 2.332 | H | Box | 6.81 | 0.83315 | * | 102 | 152 | 953 | 762 | 6.5747 | 0.81787 | 3.3853 | -0.0014081 | 0.076114 | 0.00037 | -0.0013522 |  | -0.0051487 |  | 0.82302
52 | Kinectrics 2400 | 2.3348 | H | Box | 4.787 | 0.68006 | * | 102 | 152 | 953 | 762 | 4.6967 | 0.6718 | 2.5788 | 5.5e-05 | 0.1182 | 0 | 0.0001141 |  | -0.0007392 |  | 0.67254
53 | Kinectrics 2400 | 2.345 | H | Box | 2.527 | 0.40261 | * | 102 | 152 | 953 | 762 | 2.5118 | 0.39996 | 1.3115 | -0.0043782 | 0.30585 | 0.02565 | -0.0043172 |  | 0.000168 |  | 0.39979
54 | Kinectrics 2400 | 2.3598 | H | Box | 16.403 | 1.2149 | * | 102 | 152 | 953 | 762 | 15.5385 | 1.1914 | 5.4977 | 0.0041808 | 0.16154 | 0.00847 | 0.0041572 |  | -0.006908 |  | 1.1983
55 | Kinectrics 2400 | 2.3693 | H | Box | 14.4 | 1.1584 | * | 102 | 152 | 953 | 762 | 13.6985 | 1.1367 | 5.709 | 0.0039578 | 0.13174 | 0.00577 | 0.0039186 |  | -0.0060423 |  | 1.1427
57 | Kinectrics 2400 | 2.344 | H | Box | 15 | 1.1761 | * | 102 | 152 | 953 | 762 | 13.5414 | 1.1317 | 5.0149 | -0.018143 | 0.14044 | 0.13193 | -0.01813 |  | -0.028485 |  | 1.1601